## Cover
GENSTAR EMERGENCY LIGHTING SOLUTIONS
SCHEDULE "A" - EMERGENCY LIGHTING LOGBOOK
Maintained pursuant to clause 1 and clause 7 of the Emergency Lighting Maintenance Agreement.
SITE DETAILS
Project name
Site address
Building manager
Site contact email / phone
Commissioning date
Genstar service contract ref.
Logbook ref.
5-YEAR PRODUCT WARRANTY
Warranty start date
Warranty expiry date
Coverage | Free replacement of luminaires, batteries, drivers and control gear for material or manufacturing defect during the warranty period.
Conditions | Warranty subsists for so long as this logbook is maintained per Service Contract clause 7. Lapsed or sporadic inspections may void warranty.
AT A GLANCE
Fittings on register
Tests logged
Defects open (results not OK)
GENSTAR CONTACT
Genstar Lighting (Pty) Ltd
Commerce Square Office Park, Building 3, 2nd Floor, 39 Rivonia Road, Sandhurst, 2196
Tel: (011) 321 0198 - spec@genstaremergency.co.za - www.genstaremergency.co.za

## Asset Register
ASSET REGISTER
Master list of every emergency luminaire on Site. Update on commissioning of new fittings or decommissioning of existing fittings.
Fitting ID | Area / Location | Type | Model | Install Date | Warranty Expiry | Notes
GELS#23123 | Escape Stair #1 | Self-test | GELS-EM-2W | 2023-03-04
GELS#23124 | Escape Stair #1 | Self-test | GELS-EM-2W | 2023-03-04
GELS#23125 | Escape Stair #1 | Self-test | GELS-EM-2W | 2023-03-04
GELS#23126 | Escape Stair #1 | Self-test | GELS-EM-2W | 2023-03-04
Formulas:
Warranty Expiry = IF([Install Date]="","",EDATE([Install Date],60))

## Test Log
TEST LOG
One row per fitting per test event. Use the dropdowns for Test Type and Result. Quarterly cadence alternates 3-Month Battery Test and 3-Month Luminaire Test, plus an annual full-duration discharge test (90 min) on the fourth quarterly visit.
Date | Area | Fitting ID | Test Type | Result | Remedial Action | Inspector Name | Signature
2026-07-05 | Escape Stair #1 | GELS#23123 | 3-Month Battery Test | Green Self-Test Light On - OK | n/a | (inspector)

## Guidance Notes
HOW TO USE THIS LOGBOOK
1. On commissioning
Populate the Cover sheet (project name, address, building manager, commissioning date). Genstar's commissioning engineer will issue a contract reference and logbook reference. The 5-year warranty period auto-calculates from the commissioning date.
2. Asset Register
Add every emergency luminaire and exit sign on Site to the Asset Register. Each fitting needs a unique Fitting ID, a Location, the Type (use the dropdown), the Model number, and the Install Date. Warranty Expiry calculates automatically.
3. Quarterly testing
SANS 10114-2 requires a functional test every 3 months and a full-duration discharge test every 12 months. Alternate the quarterly tests: Battery Test in Q1 and Q3, Luminaire Test in Q2, Annual Full-Duration Discharge Test in Q4. Each event must record one row per fitting on the Test Log sheet.
4. Self-test interpretation
GELS luminaires self-report status via a status LED. Green Solid = OK. Yellow blinking = battery needs checking (usually a deep-cycle reset will recover, see Remedial Action). Solid Red = luminaire failure (replace under warranty if in period). No indicator = power loss (check circuit before assuming luminaire fault).
5. Warranty
The 5-year product warranty is conditional on this logbook being maintained (Service Contract clause 7). If a fitting fails during the warranty period, Genstar replaces it free of charge. After year 5 the service contract continues but replacement luminaires are chargeable.
6. Inspector access
Under the Physical Agents Regulations 2024 (effective 5 September 2026), Department of Employment & Labour inspectors may demand sight of this logbook. Keep it accessible at the building reception with the OHS Act file. Missing or sporadic entries indicate non-compliance even if luminaires are present and working.